Public Liaison Committee (PLC) Meeting Minutes
Date: December 10, 2024
Time: 6:00 PM – 7:50 PM
Location: Hybrid (In-person and Online)
Chair: Joe Lyng
Recorder: Shannon

Attendee’s In person: Don Constable, Tim Henry, Darlene Henry, Michele Drenters, Peter Kearney, Helen Kearney, Steve Papagiannias, Vijay Kotamarti

Attendee’s Online: Isabela Hermann, Steven Kirby

1. Welcome and Introductions

- Joe Lyng opened the meeting and confirmed online participants could hear and be heard.

- Roundtable introductions were conducted. Attendees included members from Emerald Energy, Brampton Environmental Alliance, Sierra Peel, and local residents.

2. Agenda Review

- No changes or additions were made to the agenda.

- Previous minutes were unavailable due to technical issues

3. Housekeeping

- A concern was raised regarding the Charter's commitment to post meeting minutes and dates online.

- The PLC currently consists of only two active members (Don and Vijay).

- Plans are in place to formalize the committee in 2025 and re-engage participants.

- Action Item: Shannon to draft a process for Charter sign-ons (members/observers) and ensure relevant materials are posted to the website.

4. Operational Update

- 2023 saw slightly above-average waste receipts (~150,000 tonnes)

- 2024 waste receipts slightly below average; expected to normalize due to seasonality.

- International Airport waste recovering post-COVID and returning to pre-pandemic levels. International Airport waste volumes have rebounded to pre-COVID levels.

- Unacceptable waste (e.g., mattresses) continues to be a challenge, particularly from York Region.

- Bottom ash reuse is lower than expected due to equipment repairs.

- APC residue and related outputs are tracking normally.

- Electricity and steam production remain within expected parameters.

5. Emissions and Environmental Incidents

- Three reportable incidents occurred in 2024:

  - April 3: Power surge caused 23 minutes of bypass stack operation.

  - June 17: CO exceedance at stack due to burner malfunction.

  - September 24: Bird strike tripped turbine and triggered bypass stack.

- All incidents were reported to MECP with no ongoing issues.

- Stack sampling conducted early (September) with positive results:

  - Mercury, dioxins/furans, cadmium, and lead all below limits.

  - NOx emissions: 92 ppm (limit 105 ppm)

  - Particulate matter low due to recent baghouse replacements.

Question regarding the power surge and using the Turbine as a back up generator:

- The turbine is designed to isolate itself from the grid during surges, but this process is not always reliable.

- When isolation occurs, it can only hold briefly (1–2 minutes) before turbine steam destabilizes, causing the turbine and generator to trip.

- These events are considered uncontrollable external factors.

- The plant is working to improve its self-protection systems and automate the switch to “island mode” during such events.

- When the turbine disconnects from the grid, generated electricity has no outlet, causing instability and tripping the system.

- If the customer (e.g., Cascades) also trips offline, steam has nowhere to go, triggering further complications.

- Emerald is always looking for ways to improve their system.

Discussion on Emissions Stack testing

Minute Summary – Emissions Sampling and Stack Results

- Stack sampling is conducted annually, typically aligned with the baghouse filter replacement cycle.

- Bags are usually replaced every three years; it was coincidental that this year’s sampling followed a full bag replacement, leading to especially low particulate emissions.

- NOx levels were slightly elevated this year compared to previous years but remained within compliance (limit: 105 ppm; typical operation: ~90 ppm).

- NOx fluctuations are influenced by waste composition and combustion temperatures—more plastic waste can increase NOx.

- Multiple stacks in the expansion would maintain the same concentration per stack, but total loading (volume) would increase.

- Hydrochloric acid (HCl) emissions are managed by lime injection and remain within the 18 ppm limit.

- Sulfur dioxide (SO₂) emissions are also indirectly controlled by lime; not continuously monitored due to legacy design but measured during stack sampling.

6. Redevelopment Project Summary

- Full project summary of water, air, ecology, and other elements presented.

- Clarifications provided around:

  - Emissions standards based on concentration (not mass loading).

  - Increased stacks will not exceed concentration limits despite higher volume.

  - Ontario standards largely align with global standards; Ontario's dioxin/furan standard is among the strictest.

- Soil sampling for metals has shown no upward trend over 20 years.

- Suggestions made to consider increasing proposed 70m stack height to 80m for improved dispersion.

- Action Item: Emerald to discuss stack height increase with consultants and potentially revise submission.

7. Steam Line Replacement Project

- Project involves rerouting aging steam line to reduce maintenance risks.

- Estimated cost: $5–7 million.

- Archaeological review required prior to construction.

- Replacement supports renewal of steam contract with Cascades (current ends 2028; proposed renewal for 21 years).

8. Hydrogen Pilot Project

- Project received IESO approval; exploring vendor change due to membrane issues.

- Considering local company (Next Hydrogen) for alkaline process.

- Hydrogen use options being explored:

  - Fuel cell trials with Peel/York/Simcoe

  - Hydrogen injection into UPAC trucks (5-vehicle pilot proposed)

- Storage will be minimal on-site due to space constraints.

9. Backup Power and Emission Control

- Hydrogen, diesel, batteries, or natural gas may be used for backup.

- Discussions around large-scale batteries and UPS systems ongoing.

- Only critical systems (ID fans) would be powered in blackout.

- Site also evaluating rooftop solar options for offset, not backup.

10. Public Comments & Health Risk Assessments

- Concerns raised about cumulative impacts, air quality, and traffic.

- Health risk assessment by Intrinsik confirmed compliance with MECP standards.

- Reports available online; link to be circulated.

- Attendees encouraged to review Executive Summary first.

11. Environmental Screening Process

- Public comment period ends January 7, 2025.

- Comments should be submitted to MECP and Emerald.

- Ministry will assess and determine approval or further conditions.

12. Next Meeting

- Tentatively scheduled for late February 2025.

- Will provide updates on comments and next steps.

- Hybrid format expected again; space for 10 in-person attendees.

Adjournment: Meeting adjourned at 7:50 PM.

Action Items:

- Shannon to draft Charter sign-on process and update website.

- Shannon to circulate current meeting minutes.

- Emerald to evaluate feasibility of increasing stack height to 80m.

- Shannon to provide link to reports and submission instructions for public comments.

Minutes prepared by: Shannon

`